Fire Extinguisher Preventative Maintenance

# References

## Authorization

## Training/Certification

## Equipment/Information

## Policies

## Related Procedures

# Security Considerations

|  |  |  |
| --- | --- | --- |
| CM informatioin | | |
| Site/Pod: | CM#: | |
| Technician: | Date: | |
| Equipment Information | | |
| Manufacturer: | | Model #: |
| Serial #: | Assed ID: | |

# Procedure

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | FE1 | | FE2 | | FEN | |
|  | Yes | No | Yes | No | Yes | No |
| 1. Has a licensed fire extinguisher maintenance contractor inspected the extinguisher within the past 12 months? |  |  |  |  |  |  |
| 1. Was a hydrostatic test date completed within the past five years? |  |  |  |  |  |  |
| 1. Is the extinguisher visible, unobstructed, and in its designated location? |  |  |  |  |  |  |
| 1. Is the locking pin intact and the tamper seal is unbroken? |  |  |  |  |  |  |
| 1. Is the extinguisher free from obvious physical damage, corrosion, leakage, or clogged nozzle? |  |  |  |  |  |  |
| 1. Is the pressure gauge or indicator is in the operable range or position? |  |  |  |  |  |  |
| 1. Lift the extinguisher—is it still full? |  |  |  |  |  |  |
| 1. Are the operating instructions on the nameplate legible and facing outward? |  |  |  |  |  |  |
| 1. Turn fire extinguisher upside down and tap bottom with a rubber mallet—is the powder compressed? |  |  |  |  |  |  |
| 1. Did you initial and date the back of the tag? |  |  |  |  |  |  |

Corrective actions recommended or taken: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

## Document Properties

|  |  |
| --- | --- |
| **Property** | **Value** |
| Site Code | DCA |
| Filename | dca\_dceo\_pm\_fire-extinguisher |
| Title | Fire Extinguisher Preventative Maintenance |
| Version number/Date version published | Draft |
| Doc Type | PM |
| Zone | Region |
| Technical Owner | swilleye@ |
| Technical Writer | beelliot@ |
| Affected Equipment | Fire extinguisher |
| Sensitivity rating | Amazon Confidential |
| Origin | Commercial verson |
| URL | TBD |
| Physical location | TBD |
| Audience | EOT |
| Renewal date | 1/1/15 |
| Special requirements | What PPE is required for this work? |
| Safety considerations | What are the possible hazards the employee might be at risk of. |
| Physical requirements | Climb a ladder, lift over 50 lb., etc. |

## Status

|  |  |  |
| --- | --- | --- |
| **Status** | **Date mm/dd/yy** | **Approver/Reviewer Name** |
| Original filed | 1/1/14 | NA |
| Writer sent to SME for review | 1/1/14 | NA |
| SME sent to Writer | 1/1/14 | NA |
| Writer sent to SME for approval |  | NA |
| SME approved |  |  |
| Writer copy edited |  | NA |
| Site Manager approved |  |  |
| Regional Manager approved |  |  |
| Writer published |  | NA |